BUILDING PRODUCTS OTHER THAN FLOORS

EUROCLASSES ACCORDING TO NF EN 13 501	REQUIREMENTS

A1	-	-	incombustible

A2	s1	d0	MO

A2	s1	d1 (1)

A2	s2	d0
s3	d1(1)	M1

s1	d0
B	s2	d1 (1)
s3

s1 (2)	d0
C (3)	s2 (3)	d1 (1)	M2
s3 (3)

s1 (2)	d0	M3
D	s2	d1 (1)	M4
s3	(not dripping)

All classes (2) other than E-d2 and F	M4

Performance level d1 is only accepted for products which are not thermofusible in the test conditions.
  1. Performance level s1 cancels the necessity of providing the information required under the « article » dated 4th November 1975 modified, concerning reglementation of the use of certain materials and products in establishments used by members of the public and the « instruction » dated 1st November 11976 pertaining to it.
  2. Acceptable for M1 if not substantial as defined in « annexe » 1